## Summary Point Report
Gorgon Civils and Underground Services Project: | [24 empty] | Hide Columns | [5 empty] | Hide Columns |  |  |  | Hide Columns | [5 empty] | Hide Columns |  |  |  | Hide Columns |  |  |  | Hide Columns |  |  |  |  | Hide Columns | [7 empty] | Hide Columns | [8 empty] | Hide Columns
As-Built Survey:
[8 empty] | Report Date: | 2015-07-18 | [12 empty] | S:\BWI Survey Data\11 AS BUILT\2 FND LOCATION ASBUILTS |  |  | S:\BWI Survey Data\11 AS BUILT\2 FND LOCATION ASBUILTS\GAHC-GAHD-MEG-WALLS C1-BASE INSITU 141012.csv
Area: | PLANT WEST: GAHC-GAHD-MEG-WALLS C1-BASE INSITU QA | [6 empty] | Office Surveyor: | CIV | [12 empty] | (Enter the correct path for location of files) |  | Rotation Tolerance: | GAHC-GAHD-MEG-WALLS C1-BASE INSITU 141012.csv
|  |  | DWG: | [20 empty] | (User Entry) | 141012 | 12/10/2014 | [9 empty] | Calc'd from VLOOKUP (for bolts Relative & Group Centres Absolute) |  |  | From | [27 empty] | Difference Design to As-Built
| Date of Survey: | Design Information |  |  |  |  | As Built Information |  |  |  | (Survey Accuracy: ±2mm) |  | As-Built Results | [5 empty] | Bolts |  |  | NOTE: Set "Print Area" Before Printing !! | 1: | 50 | Results from VLOOKUP |  |  |  |  | Calculated from VLOOKUP (for Absolute) | [8 empty] | VLOOKUP | [7 empty] | Bolts and Bolt Group Centre Calculations | [5 empty] | Copied Bolt Group Centres |  |  |  | Radiations from Centroids | [11 empty] | Indiv. Bolts |  |  | Template
ABS Code | 12d Report File Name: | [11 empty] | (Absolute Diffs) | [5 empty] | (Relative) |  |  |  | mm/m | 50 | Item | Horiz Limit |  | Vert Limit |  | Hor Chk Limit |  | Ver Chk Limit |  | Horiz Limit | Vert Limit | Hor Chk Limit |  | Horiz Limit | delta's | Trimmed Text |  |  |  |  | Bolt Grp centre |  | Design |  | As-Built |  | Chg & Offset |  | Design |  | As-Built |  | Design |  | As-Built |  | Design |  |  | As-Built |  |  | Rotation |  | Rot Tol.(B) | Rot Tol.(A) | Rotation | Rotation (mm)
Grid Ref | 12d Design String Name: | Code | 12d Design Model | Easting | Northing | Level | Point Id | Code | 12d Model or String | Easting | Northing | Level | d.E | d.N | String | Offs | d.L | Description | ∆.E | ∆.N | Rot | Fill in yellow coloured cells | deg | 1.1458 |  | Lower | Upper | Lower | Upper | Lower | Upper | Lower | Upper | Text | Text | Lower | Upper | Text | to | Code | 12d Design Model | Point Id | Code | 12d Model | d.E | d.N | East | North | East | North | d.E | d.N | East | North | East | North | d.E | d.N | d.E | d.N | Angle | Brg | Dist | Angle | Brg | Dist | d.Brg | d.Dist | [Not Used] | [Used] | Direction | [over distance
| 12d Design Tin Name: | [11 empty] | (mm) | (mm) | Chg | (mm) | (mm) |  | (mm) | (mm) | [18 empty] | Display | [21 empty] | (deg) | (deg) |  | (deg) | (deg) |  | (deg) |  | (deg) | (deg) |  | centre to bolt]
GAHC-GAHD-MEG-WALLS | 12/10/2014 | BOC | PW MAIN 0900FND0604 0 FND | 597.705 | 513.622 | 20.1 | TPS0054 | TC | FND INSITU 141012THR1 | 597.695 | 513.613 | 20.496 | -10 | -9 |  |  | 396 | Top Conc Base (is) |  |  |  | Abs Tol Exceeded (V: -6,+0mm) |  |  | Top Conc Base (is) | -10 | 10 | -6 | 0 | -10.5 | 10.5 | -6.5 | 0.5 |  | (V: -6,+0mm) |  |  |  | ENL | BOC | PW MAIN 0900FND0604 0 FND | TPS0054 | TC | FND INSITU 141012THR1
C1-BASE | GAHC-GAHD-MEG-WALLS C1-BASE INSITU 141012.csv | BOC | PW MAIN 0900FND0604 0 FND | 610.043 | 513.622 | 20.1 | TPS0055 | TC | FND INSITU 141012THR1 | 610.041 | 513.62 | 20.509 | -2 | -2 |  |  | 409 | Top Conc Base (is) |  |  |  | Abs Tol Exceeded (V: -6,+0mm) |  |  | Top Conc Base (is) | -10 | 10 | -6 | 0 | -10.5 | 10.5 | -6.5 | 0.5 |  | (V: -6,+0mm) |  |  |  | ENL | BOC | PW MAIN 0900FND0604 0 FND | TPS0055 | TC | FND INSITU 141012THR1
|  | BOC | PW MAIN 0900FND0604 0 FND | 610.043 | 506.622 | 20.1 | TPS0002 | TC | FND INSITU 141012THR1 | 610.039 | 506.631 | 20.503 | -4 | 9 |  |  | 403 | Top Conc Base (is) |  |  |  | Abs Tol Exceeded (V: -6,+0mm) |  |  | Top Conc Base (is) | -10 | 10 | -6 | 0 | -10.5 | 10.5 | -6.5 | 0.5 |  | (V: -6,+0mm) |  |  |  | ENL | BOC | PW MAIN 0900FND0604 0 FND | TPS0002 | TC | FND INSITU 141012THR1
|  | BOC | PW MAIN 0900FND0604 0 FND | 597.705 | 506.622 | 20.1 | TPS0005 | TC | FND INSITU 141012THR1 | 597.699 | 506.636 | 20.511 | -6 | 14 |  |  | 411 | Top Conc Base (is) |  |  |  | Abs Tol Exceeded (H: -10,+10mm) (V: -6,+0mm) |  |  | Top Conc Base (is) | -10 | 10 | -6 | 0 | -10.5 | 10.5 | -6.5 | 0.5 | (H: -10,+10mm) | (V: -6,+0mm) |  |  |  | ENL | BOC | PW MAIN 0900FND0604 0 FND | TPS0005 | TC | FND INSITU 141012THR1
[47 empty] | none | none | none | none

## Tolerances
Used for VLOOKUP
TOLERANCES |  | Horizontal Limit |  | Vertical Limit |  | delta's to
Code | Item | Lower | Upper | Lower | Upper | Display |  |  |  |  | ALL CONCRETE FOUNDATION TOLERANCES TO BE CHANGED MANUALY TO FOLLOW TECHNICAL BULLETIN: TB-090 REV 0 ** ESPECIALLY MISC. FOUNDATIONS THAT CARRY DIFFERENT ITEMS **
MUST USE THESE CODES
BO | Bolt (pc) | -2 | 2 | -15 | 6 | ENL
BT | Bolt (is) | -2 | 2 | -6 | 6 | ENL |  | "BT" and/or "BO" (FOR BOLTS)
BTC | Bolt Template Centre | -6 | 6 | -99999 | 99999 | EN |  | "SC" (FOR SCABBLE)
BGCC | Bolt Grp Centre Calc | -6 | 6 | -99999 | 99999 | EN |  | "BGCC" (FOR BOLT GROUP CENTRE CALC)
CE | Plinth Face (pc) | -25 | 25 | -99999 | 99999 | EN |  |  |  |  | DOCUMENTS CAN BE FOUND HERE
COL | Plinth Level (pc) | -99999 | 99999 | -15 | 3 | L | <---- VARIES - SEE TOLERANCES | These codes are embedded inside the macro formulae.
PC | Plinth Cnr (pc) | -25 | 25 | -15 | 3 | ENL | <---- VARIES - SEE TOLERANCES
PT | Plinth Top (is) | -25 | 25 | -15 | 3 | ENL | [5 empty] | PRECAST QA
PTL | Plinth Level (is) | -99999 | 99999 | -6 | 0 | L | [5 empty] | INSITU QA
SC | Scabble Level | -99999 | 99999 | -99999 | 99999 | L
SK | Shear Key (is) | -25 | 25 | -15 | 0 | ENL |  |  | PT/TC | Insitu with Shear Key TOLERANCE = +-25mm Hz/ +0 -15mm V (for base and plinth)
TC | Top Conc Base (is) | -10 | 10 | -6 | 0 | ENL | <---- VARIES - SEE TOLERANCES |  |  | Insitu without Shear Key TOLERANCE = +-10mm Hz/ +0 -6mm V (for base and plinth)
TCB | Top Conc Base (pc) | -25 | 25 | -15 | 3 | ENL | <---- VARIES - SEE TOLERANCES
TCL | Conc Level (is) | -99999 | 99999 | -6 | 0 | L | <---- VARIES - SEE TOLERANCES
WT | Wall Top | -10 | 10 | -6 | 0 | ENL
WF | Wall Face | -10 | 10 | -99999 | 99999 | EN
WB | Wall Bottom | -10 | 10 | -6 | 0 | ENL
LIP | Wall Lip | -10 | 10 | -6 | 0 | ENL
WTL | Wall Top Level | -99999 | 99999 | -6 | 0 | L
PLT | Embedded Plate | -3 | 3 | -3 | 3 | ENL | <---- VARIES - SEE TOLERANCES
LU | Top "L" Trench Unit | -50 | 50 | -12 | 12 | ENL
DB | Top of Duct Bank | -50 | 50 | -12 | 12 | ENL
PKT | Pocket (is) | -10 | 10 | -6 | 0 | ENL
BTL | Bolt Level (is) | -99999 | 99999 | -15 | 6 | L
BOL | Bolt Level (pc) | -99999 | 99999 | -15 | 6 | L
BTO | Bolt Template Orient. | -99999 | 99999 | -99999 | 99999
BED | Bedding | -99999 | 99999 | 50 | 50 | ENL
IL | Invert "U" drain | -99999 | 99999 | -15 | 15 | L
CC | Conc Drainage Channel | -25 | 25 | -15 | 0 | ENL | <-- IF FINISHED SURFACE IS NOT PAVED THE VERT TOLERANCE IS +/-12mm. IF THE CHANNEL IS IN A CONC PAVED AREA ITS +0/-6mm
CBS | Culvert Base Slab | -25 | 25 | -10 | 10 | ENL | <-- Precast Base Unit for BOX CULVERT -Tolerence from AS1597.2 + 10.4.5 on SPC 1048
CBU | Culvert Box Unit | -25 | 25 | -10 | 10 | ENL | <-- Precast Culvert Unit - Tolerence from AS1597.2 + 10.4.5 on SPC 1048
HCI | Halfen Channel (is) | -2 | 2 | -6 | 6 | ENL | <-- Halfen Tolerances from Bolt Tolerances (ONLY REPORT THE EASTING OR THE NORTHING)
HCP | Halfen Channel (pc) | -2 | 2 | -15 | 6 | ENL | <-- Halfen Tolerances from Bolt Tolerances (ONLY REPORT THE EASTING OR THE NORTHING)
FSU | Final Stub-up | -99999 | 99999 | -99999 | 99999
is= In-Situ
pc = Precast

## Sketch (In-Situ)
IN-SITU BLOCKS (with Shear Key)
[ 12d Point to Point Reports ]
(z only)
(z only - attach to SK or PT)
(x,y or x,y,z)
(x,y or x,y,z)
(x,y,z)
IN-SITU BLOCKS (with Bolts)
[ 12d Point to Point Reports ]
(z only - attach to BT)
(x,y or x,y,z)
(z only - attach to PT)
(x,y or x,y,z)
(x,y,z)
PT (Plinth Top)
SC (Scabble)
PTL (Plinth Level)
SK (Shear Key)
PT (Plinth Top)
TC (Top Conc)
PTL (Plinth Level)
BT (Bolt)
TC (Top Conc)
BTL (Bolt Level)
INSITU
INSITU

## Sketch (PreCast) rev.2
PRECAST BLOCKS (with Shear Key)
[ 12d String Offset Reports ]
(z only)
(z only)
(x,y only)
PRECAST BLOCKS (with Bolts) |  | (rev.2)
[ 12d String Offset Reports ]
[ 12d Point to Point Reports ]
|  |  | (z only) | (z only - attach to BO)
(x,y or x,y,z)
(z only - attach to PC)
(x,y only)
CE (Plinth face)
SC (Scabble)
COL (Plinth Level)
COL (Plinth Level)
BO (Bolt)
BTL (Bolt Level)
PRECAST
PRECAST
SC (Scabble)
CE (Plinth face)

## OLD--Sketch (PreCast)
PRECAST BLOCKS (with Shear Key)
[ 12d String Offset Reports ]
(z only)
(z only)
(x,y only)
PRECAST BLOCKS (with Bolts)
[ 12d Point to Point Reports ]
(z only - attach to BO)
(x,y or x,y,z)
(z only - attach to PC)
(x,y or x,y,z)
(x,y,z)
CE (Plinth face)
SC (Scabble)
COL (Plinth Level)
PC (Plinth Cnr)
COL (Plinth Level)
BO (Bolt)
BTL (Bolt Level)
PRECAST
PRECAST
TCB (Top Conc)

## AREAS
FOUNDATION TYPE | AREA | ABS | AREA | LOGGED ON USER | ALIAS | INITIALS |  | 150718
INSITU QA | TRAIN 1: | AAA | AGRU | gsurveyc | paumoore | PM
PRECAST QA | TRAIN 2: | ABA | AGRU | CIV | gsurveye | EL | PLANT WEST MISC FND C1-BASE INSITU QA 150718
- | TRAIN 3: | ACA | AGRU |  | aloosley | AJL
| EWC: | CAA | AGRU |  | gsurveyc | CIV
| PLANT EAST: | CBA | AGRU
| MOF: | CCA | AGRU
| PLANT WEST: | RBC | AGRU
| AGRU: | SAN | AGRU
| GTG: | UAH | AGRU
| G-FLARE: | TAA | TRAIN 1
| - | TAB | TRAIN 1
|  | TAC | TRAIN 1
|  | TAD | TRAIN 1
PRECAST QA |  | TAE | TRAIN 1
| 7 | TAF | TRAIN 1
| MOF: | TAG | TRAIN 1
|  | TAH | TRAIN 1
|  | TAJ | TRAIN 1
|  | TBA | TRAIN 2
|  | TBB | TRAIN 2
|  | TBC | TRAIN 2
|  | TBD | TRAIN 2
|  | TBE | TRAIN 2
GAH |  | TBF | TRAIN 2
PLANT WEST |  | TBG | TRAIN 2
|  | TBH | TRAIN 2
|  | TBJ | TRAIN 2
INSITU QA |  | TCA | TRAIN 3
|  | TCB | TRAIN 3
|  | TCC | TRAIN 3
|  | TCD | TRAIN 3
|  | TCE | TRAIN 3
|  | TCF | TRAIN 3
|  | TCG | TRAIN 3
|  | TCH | TRAIN 3
|  | TCJ | TRAIN 3
|  | WAA | GTG
|  | WAB | GTG
|  | WAC | GTG
|  | WAD | GTG
|  | WAE | GTG
|  | WAF | GTG
|  | WAG | GTG
|  | WAH | GTG
|  | WAJ | GTG
|  | WAK | GTG
|  | WAL | GTG
|  | WAN | GTG
|  | DAA | EWC
|  | GAD | EWC
|  | GAE | EWC
|  | UAC | EWC
|  | UAE | EWC
|  | UAF | EWC
|  | UAG | EWC
|  | UAL | EWC
|  | RBD | EWC
|  | TAJ | TRAIN 1
|  | TBJ | TRAIN 2
|  | TCJ | TRAIN 3
|  | EAA | G-FLARE
|  | EAB | G-FLARE
|  | SAT | PLANT EAST
|  | DAB | PLANT EAST
|  | RBF | PLANT EAST
|  | RBH | PLANT EAST
|  | SAD | PLANT EAST
|  | SAE | PLANT EAST
|  | SAF | PLANT EAST
|  | SAG | PLANT EAST
|  | SAH | PLANT EAST
|  | SAP | PLANT EAST
|  | SAQ | PLANT EAST
|  | SAR | PLANT EAST
|  | SAS | PLANT EAST
|  | SAU | PLANT EAST
|  | SAW | PLANT EAST
|  | SBF | PLANT EAST
|  | SCA | MOF
|  | SCB | MOF
|  | SCC | MOF
|  | VAA | PLANT EAST
|  | VAB | PLANT EAST
|  | VAC | PLANT EAST
|  | GAA | PLANT WEST
|  | GAB | PLANT WEST
|  | GAC | PLANT WEST
|  | GAG | PLANT WEST
|  | GAH | PLANT WEST
|  | JAA | PLANT WEST
|  | JAB | PLANT WEST
|  | JAC | PLANT WEST
|  | JAD | PLANT WEST
|  | RBA | PLANT WEST
|  | RBB | PLANT WEST
|  | RBG | PLANT EAST
|  | UAM | PLANT WEST